## Maintenance Factor
Appendix B1
Lighting Design Maintenance Factor Calculator
V1 - 15/10/2020
1. Instructions: Only enter data into the unshaded (white) cells. Items 1.5 to 1.8 contain drop down selection lists - Select the relevant material and the associated factor will automtically be entered in the fourth column. Once all values are entered and the worksheet is saved, the calculation will update to show the final result in the pink shaded cells. The Design Maintenance Factor shall be used for design calculations.
ITEM | TOPIC | MATERIAL | ACTUAL VALUE
1 | Lumen Depreciation | NA | NA
1.1 | Provide LM-80-08 report for the proposed 4000K LED chip | NA | NA
1.2 | Provide TM 21-11 analysis [Using EPA Calculator and In-Situ Temperature Measurement Testing (ISTMT){for a complete luminaire}]. URL:https://cmadmin.energystar.gov/sites/default/files/asset/document/ENERGY%20STAR%20TM-21%20Calculator%20rev%20%2006-18-2018.xlsx. The Analysis is required for the LED-driver combination with the highest lumen output-junction temperature configuration for the proposed luminaire. {NOTE: The "Case Temperature (TC)" input required in the spreadsheet is measured at the test point (TS) used in the LM80 test and the ISTMT test - usually a solder point beside the chip} | NA | NA
1.3 | Lamp Lumen Maintenance Factor (LLMF) at 85,000 hrs (total luminaire energised time) & 25C from analysis in item 1.2 {Note: A minimum of 0.90 is required} | NA
1.4 | Luminaire Electronic Failure (LEF) – Estimated deterioration in total luminaire light output due to degradation or failure of electronic components [PCB electronics, Driver electronics, terminations, solder joints, PCB connections, wiring and the like]. | NA | 0.99
1.5 | Luminaire Optical Depreciation for Visor (LODV). {Note: Select material from drop down list} |  | #N/A
1.6 | Luminaire Optical Depreciation for Reflector (LODR). {Note: Select material from drop down list} |  | #N/A
1.7 | Luminaire Optical Depreciation for Lens (LODL). {Note: Select material from drop down list} |  | #N/A
1.8 | Luminaire Maintenance Factor (LMF) |  | #N/A
1.9 | Theoretical Maximum Maintenance Factor (MF) [= LLMF x LEF x LODV x LODR x LODL x LMF] | NA | #N/A
1.10 | Design Maintenance Factor (MF) {NOTE: Capped by automated formula to 0.80 maximum as per AS/NZS1158} | NA | #N/A
OPTICAL MATERIALS LOOK UP TABLES
Visor Material
| Nil (No visor) |  | 1
| Toughened glass or silicone |  | 1
| UVS-PMMA (Acrylic) |  | 0.91
| UVS-PC (Polycarbonate) |  | 0.69
Reflector Material
| Nil (No reflector) |  | 1
| Aluminium (behind glass visor) |  | 0.99
| Aluminium (behind PMMA visor) |  | 0.99
| Aluminium (behind PC visor) |  | 0.99
| Metalised PC (behind glass visor) |  | 0.97
| Metalised PC (behind PMMA visor) |  | 0.96
| Metalised PC (behind PC visor) |  | 0.96
Lens Material
| Nil (No lens) |  | 1
| Glass |  | 1
| Silicone |  | 1
| UVS-PMMA (exposed) |  | 0.91
| UVS-PMMA (behind glass visor) |  | 0.99
| UVS-PMMA (behind PMMA visor) |  | 0.99
| UVS-PMMA (behind PC visor) |  | 0.99
| UVS-PC (exposed) |  | 0.69
| UVS-PC (behind glass visor) |  | 0.97
| UVS-PC (behind PMMA visor) |  | 0.96
| UVS-PC (behind PC visor) |  | 0.96
Visor type for LMF
| Visor |  | 0.92
| Exposed (No visor) |  | 0.78

## Revision
Revision Table
Version | Date | Changes
1 | 2020-10-15 | Original